Rotor blade inspection report

| Overview WTG data |  |  |
| --- | --- | --- |
| Wind Farm |  | Meerwind Süd / Ost |
| Location |  | Esjberg |
| WTG model |  | Siemens 3.6 MW |
| WTG number |  |  |
| WTG ID |  |  |
| Customer |  | WindMW Service GmbH Schleusenstraße 12 D - 27568 Bremerhaven |
| Inspection type |  | External blade inspection |

| Overview rotor blades |  |  |
| --- | --- | --- |
| Blade type | B58 |  |
| Set number |  |  |
| Blade number A |  |  |
| Blade number B |  |  |
| Blade number C |  |  |
| Date of Inspection |  |  |
| Service company | GMA Werkstoffprüfung GmbH |  |
| Name of Inspectors |  |  |
| Inspection type (e.g. EOW, regular inspection) | External blade inspection EOW |  |

# Inspection results

| Damage ID |  |
| --- | --- |
| Area: |  |
| Description |  |
| Category: |  |
| Comments |  |

## Inspection results of blade B, number: 580438200 outside

| # Finding | Position: Side /Edge | LE | DF from | 44 | PD in [%] from | 0 | Size in [mm] | 1000x50 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 580438200-1 | Category | 2 | to in [m] | 45 | to | 0 | Depth in [mm] | n.a. |
| Damage description e.g. damaged layers, affected area (bonding) |  | leading edge erosion; on surface laminate |  |  |  |  |  |  |
| Overview picture |  |  | Detailed picture (visible scale!) |  |  | Optional picture |  |  |
| Comment of inspector: |  |  |  |  |  |  |  |  |
| # Finding | Position: Side /Edge | LE | DF from | 48 | PD in [%] from | 0 | Size in [mm] | 4000x50 |
| 580438200-2 | Category | 2 | to in [m] | 52 | to | 0 | Depth in [mm] | n.a. |
| Damage description e.g. damaged layers, affected area (bonding) |  | leading edge erosion; on surface coating |  |  |  |  |  |  |
| Overview picture |  |  | Detailed picture (visible scale!) |  |  | Optional picture |  |  |
| Comment of inspector: |  |  |  |  |  |  |  |  |

## Inspection results of blade B, number: 580438200 outside

| # Finding | Position: Side /Edge | LE | DF from | 52 | PD in [%] from | 0 | Size in [mm] | 6000x70 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 580435800-1 | Category | 3 | to in [m] | 58 | to | 0 | Depth in [mm] | n.a. |
| Damage description e.g. damaged layers, affected area (bonding) |  | leading edge erosion; on multilayer laminate |  |  |  |  |  |  |
| Overview picture |  |  | Detailed picture (visible scale!) |  |  | Optional picture |  |  |
| Comment of inspector: |  |  |  |  |  |  |  |  |

## Inspection results of blade C, number: 580341900 outside

| # Finding | Position: Side /Edge | LE | DF from | 44 | PD in [%] from | 0 | Size in [mm] | 8000x50 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 580341900-1 | Category | 2 | to in [m] | 52 | to | 0 | Depth in [mm] | n.a. |
| Damage description e.g. damaged layers, affected area (bonding) |  | leading edge erosion; on surface coating |  |  |  |  |  |  |
| Overview picture |  |  | Detailed picture (visible scale!) |  |  | Optional picture |  |  |
| Comment of inspector: |  |  |  |  |  |  |  |  |
| # Finding | Position: Side /Edge | LE | DF from | 52 | PD in [%] from | 0 | Size in [mm] | 6000x70 |
| 580341900-2 | Category | 3 | to in [m] | 58 | to | 0 | Depth in [mm] | n.a. |
| Damage description e.g. damaged layers, affected area (bonding) |  | leading edge erosion; on multilayer laminate |  |  |  |  |  |  |
| Overview picture |  |  | Detailed picture (visible scale!) |  |  | Optional picture |  |  |
| Comment of inspector: |  |  |  |  |  |  |  |  |

# Results of measurement of the LPS

| Measurement device type |  | Last calibration date |  |
| --- | --- | --- | --- |
|  |  | Calibration expire date |  |

## Inspection results of blade A, number: 580435800 outside

NOTE: Receptor- and equipotential bonding- numbering starts from the blade root to tip. (Receptor 1 is close to root)

| Position: Side /Edge | DF: | DF: | DF: | DF: |
| --- | --- | --- | --- | --- |
|  | Receptor 1 | Receptor 2 | Receptor 3 | Receptor 4 |
| PS |  |  |  |  |
| Ohm Ω: | 0.012 | 0.020 | 0.129 | 0.024 |
| PS |  |  |  |  |
| SS |  |  |  |  |
| Ohm Ω: | 0.012 | 0.020 | 0.129 | 0.024 |
| SS |  |  |  |  |

## Inspection results of blade B, number: 580438200 outside

NOTE: Receptor- and equipotential bonding- numbering starts from the blade root to tip. (Receptor 1 is close to root)

| Position: Side /Edge | DF: | DF: | DF: | DF: |
| --- | --- | --- | --- | --- |
|  | Receptor 1 | Receptor 2 | Receptor 3 | Receptor 4 |
| PS |  |  |  |  |
| Ohm Ω: | 0.049 | 0.022 | 0.029 | 0.027 |
| PS |  |  |  |  |
| SS |  |  |  |  |
| Ohm Ω: | 0.048 | 0.022 | 0.029 | 0.027 |
| SS |  |  |  |  |

## Inspection results of blade C, number: 580341900 outside

NOTE: Receptor- and equipotential bonding- numbering starts from the blade root to tip (Receptor 1 is close to root)

| Position: Side /Edge | DF: | DF: | DF: | DF: |
| --- | --- | --- | --- | --- |
|  | Receptor 1 | Receptor 2 | Receptor 3 | Receptor 4 |
| PS |  |  |  |  |
| Ohm Ω: | 0.013 | 0.019 | 0.024 | 0.023 |
| PS |  |  |  |  |
| SS |  |  |  |  |
| Ohm Ω: | 0.012 | 0.019 | 0.019 | 0.024 |
| SS |  |  |  |  |

| The author of an Inspection Report approves that the works were done and documented in all conscience. All work steps were done according to the provided instructions. |  |  |
| --- | --- | --- |
| This report was completed by: Name & digital signature: | Rado |  |
| Protocol number: Company: | 20200819_E_80 GMA Werkstoffprüfung |  |
| Location / Date: | Stade / 28.08.2020 |  |